Questions and answers following the pre-proposal visit to replace the boilers. / PR11455967

- Q: Supply and return pipe diameter and class?

A: Steel pipe DN80 (3’’ SCH40), fittings Class 150

- Q: Principal diagram?

A: Kindly find in below the principal diagram:

- Q: Exhaust flue diameter and length?

A: The diameter is 150mm. The length of the chimney exhaust flues is 4.40m starting from the roof ground.

- Q: Add a new exhaust condensate drain on the exhaust flue of the second boiler (as per the 1st boiler)?

A: Yes, to be added by the contractor exactly like in the 1st boiler exhaust flue.

- Q: Nameplate of the old boilers?

A: Kindly find in below the nameplate of the old boilers

- Q: Boilers power supply?

A: Power supply: 230V

- Q: BAS integration module?

A: BACNET protocol